## Gases
General Requirements for Storage and Dispense
TI ESH STANDARD 03.02 - Appendix A: Gas Matrix |  |  |  |  | NFPA Rankings / Chemical Properties | [6 empty] | Gas Cylinders & Gas Cylinder Cabinets | [14 empty] | Ventilated Enclosures (VMBs, Tool Gas Boxes and Enclosures Containing Mechanical Connections) | [13 empty] | Breathing Zone (Work Station) |  |  |  | Piping
Chemical Name | Chemical Formula | Pyrophoric Concentration | Health | Fire | Reactivity | Special Instructions | NFPA Classification | Chemicals To Avoid (Incompatibilities) | LC50 (see note 5) | Odor Threshold | Cabinet for Storage and/or Dispense (See Note 7) | Gas Leak Detection (See Note 8) | Shutdown Delay Allowed (Time) (See Note 9) | Critical Level - Required Shutdown Level (See Note 10) | Warning Level - Recommended Minimum Detection Level for the Monitor (See Note 11) | Local Alarm - At Point of Detection (See Note 8) | Automatic Sprinkler System (See Note 13) | Auto Purge/Switch Capability (See Note 14) | Exhaust (Rate) (See Note 15) | Remote Exhaust Monitoring (See Note 16) | Loss of Exhaust Response (See Note 17) | Visual Exhaust Indicator (See Note 18) | Pneumatic Cylinder Valves (See Note 19) | Restricted Flow Orifice -RFO (Size in mm/inches) (See Note 20) | EMO Capability (See Note 26) | Ventilated Enclosure Required (See Note 7) | Gas Leak Detection (See Note 8) | Shutdown Delay Allowed (Time) (See Note 9) | Critical Level - Required Shutdown Level (See Note 10) | Warning Level - Recommended Minimum Detection Level for the Monitor (See Note 11) | Local Alarm - At Point of Detection (See Note 8) | Exhaust (Rate) (See Note 15) | Remote Exhaust Monitoring (See Note 16) | Loss of Exhaust Response (See Note 17) | Visual Exhaust Indicator (See Note 18) | Pneumatic Valves (Lines >15 psi Operating Pressure) (See Note 19) | Manual Valve Per Line (See Note 21) | EMO Capability (See Note 26) | Gas Leak Detection (See Note 8) | Shutdown Delay Allowed (Time) (See Note 9) | Evacuation Level (See Note 22) | Warning Level - Recommended Minimum Detection Level for the Monitor (See Note 11) | Exhausted Enclosures | Excess Flow Control (See Note 23) | Continuous Vent Line N2 Purge (See Note 24) | Double Containment (See Note 25) | Special Notes
Acetylene | C2H2 | N/A | 0 | 4 | 3 |  | Flammable (F4) | Strong oxidizers, calcium hypochlorite, metals, halogens, hydrides, ozone, perchloric acid, potassium. | N/A | N/A | Yes | Yes | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | Yes1 | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Negative | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes2 | No | No | Gas leak detection required unless "worse-case leak" cannot exceed 25% LFL in the ventilated enclosure.1 If gas leak detection is provided, excess flow control is not required.2
Ammonia | NH3 | N/A | 3 | 1 | 0 |  | Non-Flammable Gas | Acids, combustible materials, metals, oxidizing materials, metal salts, halocarbons, halogens, amines, reducing agents, cyanides, bases | 4000 ppm | 300-500 ppb | Yes | No 1 | N/A | N/A | N/A | No | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | No 1 | N/A | N/A | N/A | No | Negative | No | N/A | No | No | Yes | Yes | No | N/A | N/A | N/A | N | Yes2 | Yes | No | Leak detection should be considered for equipment protection.1 If gas leak detection is provided, excess flow control is not required.2
Argon/Xenon/Neon | Ar/Xe/Ne | N/A | 0 | 0 | 0 |  | Simple Asphyxiant | None | N/A | N/A | N/A | [14 empty] | N/A | [12 empty] | N/A |  |  |  |  | N/A
>1% Arsine "Hi-Pressure" | >1% AsH3 | N/A | 4 | 4 | 2 |  | Highly Toxic (H4) Flammable (F4) Unstable Reactive (R2) | Bromine, potassium permanganate, sodium hypochlorite, mild to strong oxidizers, acids, halogens | 20 ppm | 200-600 ppb | Yes | Yes | Yes (10 min.) | 1.5 ppm | 25 ppb | Yes | Yes | Yes | 200 lfpm avg. (150 lfpm min.) | Yes | Alarm Only | Yes | Yes | Yes1 | Yes | Yes | Yes | Yes (10 min.) | 1.5 ppm | 25 ppb | Yes | 200 lfpm avg. (150 lfpm min.) | Yes | Alarm Only | Yes | Yes | Yes | Yes | Yes | 15 mins (Time delay of 15 mins is applicable at evacuation level of 15 ppb). Evacuation at 25 ppb should be programmed with no time delay. | 15 ppb with 15 min time delay and 25 ppb | 10 ppb | Y | Yes | No | Yes | The RFO shall be sized no greater than 110% the maximum flow required for production.1
50 ppm Arsine in Hydrogen | 50 ppm AsH3 in H2 | N/A | 3 | 4 | 1 |  | Flammable (F4) | Bromine, potassium permanganate, sodium hypochlorite, mild to strong oxidizers, acids, halogens, bromine fluoride, nitrile fluoride | 400,000 ppm | 200-600 ppb | Yes | Yes | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | Yes3 | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Negative | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes4 | No | No | If monitoring for H2, this level results in a concentration of 500 ppb of AsH3.1 1000 ppm H2 equals 50 ppb of AsH3 in concentration.2 Gas leak detection required unless "worse-case leak" cannot exceed 25% LFL in the ventilated enclosure.3 If gas leak detection is provided, excess flow control is not required.4
60 ppm Arsine in Hydrogen | 60 ppm AsH3 in H2 | N/A | 3 | 4 | 1 |  | Flammable (F4) | Bromine, potassium permanganate, sodium hypochlorite, mild to strong oxidizers, acids, halogens, bromine fluoride, nitrile fluoride | ~333,333 ppm | 200-600 ppb | Yes | Yes | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | Yes3 | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Negative | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes4 | No | No | If monitoring for H2, this level results in a concentration of 600 ppb of AsH3.1 825 ppm H2 equals 49.5 ppb of AsH3 in concentration.2 Gas leak detection required unless "worse-case leak" cannot exceed 25% LFL in the ventilated enclosure.3 If gas leak detection is provided, excess flow control is not required.4
0.06% Arsine in Hydrogen | 0.06% AsH3 in H2 | N/A | 3 | 4 | 1 |  | Flammable (F4) | Bromine, potassium permanganate, sodium hypochlorite, mild to strong oxidizers, acids, halogens, bromine fluoride, nitrile fluoride | 33,333 ppm | 200-600 ppb | Yes | Yes | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | Yes3 | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Negative | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes4 | No | No | If monitoring for H2, this level results in a concentration of 6 ppm of AsH3.1 82.5 ppm H2 equals 49.5 ppb of AsH3 in concentration.2 Gas leak detection required unless "worse-case leak" cannot exceed 25% LFL in the ventilated enclosure.3 If gas leak detection is provided, excess flow control is not required.4
50 ppm Arsine in Nitrogen | 50 ppm AsH3 in N2 | N/A | 3 | 0 | 1 |  | Simple Asphyxiant | Bromine, potassium permanganate, sodium hypochlorite, mild to strong oxidizers, acids, halogens | 400,000 ppm | 200-600 ppb | N/A | [14 empty] | N/A | [12 empty] | N/A |  |  |  | N/A | N/A
>1% Arsine "SDS" | >1% AsH3 | N/A | 4 | 4 | 0 |  | Highly Toxic (H4) Flammable (F4) Unstable Reactive (R2) | Bromine, potassium permanganate, sodium hypochlorite, mild to strong oxidizers, acids, halogens | 20 ppm | 200-600 ppb | Yes1 | Yes1 | (Alarm Only)1 | 1.5 ppm | 25 ppb | Yes | Yes1 | N/A1 | 200 lfpm avg. (150 lfpm min.) | No1 | N/A1 | Yes | N/A1 | N/A1 | Yes | Yes | Yes | Yes (10 min.) | 1.5 ppm | 25 ppb | Yes | 200 lfpm avg. (150 lfpm min.) | Yes | Alarm Only | Yes3 | Yes | Yes | Yes | Yes | 15 mins (Time delay of 15 mins is applicable at evacuation level of 15 ppb). Evacuation at 25 ppb should be programmed with no time delay. | 15 ppb with 15 min time delay and 25 ppb | 10 ppb | N/A | N/A4 | N/A4 | N/A4 | This is referencing the storage of SDS and Uptime cylinders.1 22,500 ppm equates to 1/2 the LFL of AsH3.2 The tool monitoring the exhaust meets this requirement, if provided.3 SDS and Uptime systems have proprietary designs that meet these requirements.4
Boron Trichloride | BCl3 | N/A | 3 | 0 | 1 |  | Corrosive (H3) | Aniline, phosphine, nitrogen dioxide, grease, organic compounds, strong oxidizers, strong bases, alcohol, most metals, potassium permanganate, sodium metal, fluorine, metal acetylides or carbides, acetic anhydride, ammonia and ammonia hydroxide, caustics, oleum and sulfuric acid, perchloric acid. | 2541 ppm | 1-5 ppm | Yes | No 1 | N/A | N/A | N/A | N/A | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | No 1 | N/A | N/A | N/A | N/A | Negative | N/A | N/A | No | No | Yes | Yes | No | N/A | N/A | N/A | N/A | Yes2 | Yes | N/A | Leak detection should be considered for equipment protection.1 If gas leak detection is provided, excess flow control is not required.2
>40% Boron Trifluoride "Hi-Pressure" | >40 % BF3 | N/A | 4 | 0 | 1 |  | Corrosive (H3) Toxic poor warning properties (H3) | Polymerizable materials, water, alkali metals, and all alkaline earth metals except magnesium, strong bases, glass, ceramics, silicon-based compounds, metals. | 806 ppm | 1.5 ppm | Yes | Yes | Yes (30 min.) | 12.5 ppm | 0.05 ppm | Yes | Yes | No | 200 lfpm avg. (150 lfpm min.) | No | N/A | Yes | No | No | Yes | Yes | Yes | Yes (30 min.) | 12.5 ppm | 0.05 ppm | Yes | 200 lfpm avg. (150 lfpm min.) | No | N/A | No | Yes | Yes | Yes | Yes | No | 0.5 ppm | 0.05 ppm | Y | Yes1 | Yes | N/A | If gas leak detection is provided, excess flow control is not required.1
>40% Boron Trifluoride "VAC or Uptime" | >40% BF3 | N/A | 4 | 0 | 1 |  | Corrosive (H3) Toxic poor warning properties (H3) | Polymerizable materials, water, alkali metals, and all alkaline earth metals except magnesium, strong bases, glass, ceramics, silicon-based compounds, metals. | 806 ppm | 1.5 ppm | Yes1 | Yes1 | (Alarm Only)1 | 12.5 ppm | 0.05 ppm | Yes | Yes1 | N/A1 | 200 lfpm avg. (150 lfpm min.) | No1 | N/A1 | Yes | N/A1 | N/A1 | Yes | Yes | Yes2 | Yes (30 min.) | 12.5 ppm | 0.05 ppm | Yes | 200 lfpm avg. (150 lfpm min.) | No | N/A | Yes3 | Yes | Yes | Yes | Yes | No | 0.5 ppm | 0.05 ppm | N/A | N/A4 | N/A4 | N/A4 | This is referencing the storage of VAC or Uptime cylinders.1 If the tool gas box has exhaust monitoring provided, gas leak detection for sub-atmospheric BF3 is not required.2 The tool monitoring the exhaust meets this requirement, if provided.3 VAC and Uptime systems have proprietary designs that meet these requirements.4
Carbon Dioxide | CO2 | N/A | 1 | 0 | 0 |  | Non-Flammable Gas | Powdered aluminum, beryllium, cerium alloys, chromium, magnesium-aluminum alloys, manganese, thorium, titanium, zirconium, cesium oxide, metal acetylides. | N/A | Odorless | N/A | [14 empty] | N/A | [12 empty] | N/A |  |  |  |  | N/A
Carbon Monoxide | CO | N/A | 3 | 4 | 0 |  | Flammable (F4) | Strong oxidizers, metal oxides, nickel, iron, chromium, alkali and alkaline earth metals, aluminum powder, iodine heptafluoride, sulfur, bromine, bromine trifluoride, bromine pentafluoride, chlorine dioxide, peroxodisulfuryl difluoride. | 3760 ppm | Odorless | Yes | Yes | Yes (30 min.) | 600 ppm | 12.5ppm | Yes | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | Yes1 | Yes (30 min.) | 600 ppm | 12.5ppm | Yes | Negative | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes2 | No | N/A | Gas leak detection required unless "worse-case leak" cannot exceed 25% LFL in the ventilated enclosure.1 If gas leak detection is provided, excess flow control is not required.2
Carbon Tetrafluoride | CF4 | N/A | 0 | 0 | 0 |  | Simple Asphyxiant | Metals | N/A | N/A | N/A | [14 empty] | N/A | [12 empty] | N/A |  |  |  |  | N/A
Chlorine | Cl2 | N/A | 4 | 0 | 0 |  | Toxic (H3) Oxidizer | Water, most metals, liquid or solid hydrocarbons, hydrocarbon gases, nitrogen compounds, phosphorous, boron, active carbon, silicon, alcohols, flammable liquids, flammable solids, flammable gases. | 293 ppm | 60 ppb | Yes | No 1 | N/A | N/A | N/A | N/A | Yes | No | Negative | No | N/A | Yes | No | No | Yes | Yes | No 1 | N/A | N/A | N/A | N/A | Negative | No | N/A | No | No | Yes | Yes | No | N/A | N/A | N/A | N | Yes2 | Yes | No | Leak detection should be considered for equipment protection.1 If gas leak detection is provided, excess flow control is not required.2
>4% Diborane | >4% B2H6 | 1.6% | 4 | 4 | 3 |  | Highly Toxic (H4) Pyrophoric (F4) Water Reactive (W, R3) | Moisture in air, tetravinyl lead, octanol oximine, sodium hydroxide mixtures, benzene, halocarbon liquids, strong oxidizers, boron hydrides, aluminum, lithium. | 80 ppm | 1.77-3.54 ppm | Yes | Yes | Yes (10 min.) | 7.5 ppm | 0.05ppm | Yes | Yes | Yes | 200 lfpm avg. (150 lfpm min.) | Yes | Alarm Only | Yes | Yes | Yes (≤0.25 mm/0.01in)1 | Yes | Yes | Yes | Yes (10 min.) | 7.5 ppm | 0.05ppm | Yes | 200 lfpm avg. (150 lfpm min.) | Yes | Alarm Only | Yes | Yes | Yes | Yes | Yes | Yes (5 min.) | 0.1ppm | 0.05ppm | N | Yes | Yes | Yes | RFO size limitation is for indoor storage/dispense. For exterior storage/dispense, RFO size shall not exceed 3.175 mm/0.125 in.1
~40 ppm Diborane in Hydrogen | ~40 ppm B2H6 in H2 | 1.6% | 2 | 4 | 0 |  | Flammable (F4) | Water, oxidizing agents, ammonia, alcohols, fresh metallic aluminum, lithium, halogens, halogenated compounds, octanol oxime, sodium hydroxide, benzene vapor, nitric acid, chlorine, metal oxides. | 2,000K ppm | 1.77-3.54 ppm | Yes | Yes | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | Yes3 | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Negative | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes4 | No | No | If monitoring for H2, this level results in a concentration of 400 ppb of B2H6.1 2500 ppm H2 equals 100 ppb of B2H6 in concentration.2 Gas leak detection required unless "worse-case leak" cannot exceed 25% LFL in the ventilated enclosure.3 If gas leak detection is provided, excess flow control is not required.4
~0.8% Diborane in Nitrogen | ~0.8% B2H6 in N2/Ar/He | 1.6% | 2 | 0 | 0 |  | Non-Flammable Gas | Water, oxidizing agents, ammonia, alcohols, fresh metallic aluminum, lithium, halogens, halogenated compounds, octanol oxime, sodium hydroxide, benzene vapor, nitric acid, chlorine, metal oxides. | >8000 ppm | 1.77-3.54 ppm | N/A | [14 empty] | N/A | [12 empty] | N/A |  |  |  |  | N/A
"DCS" - Dichlorosilane | SiH2Cl2 | See Special Note Section | 4 | 4 | 2 |  | Toxic (H3) Flammable (F4) Water Reactive (W, R2) | Water, strong bases, strong oxidizers, alcohols. | 314 ppm | 1-5 ppm | Yes | Yes | Yes (30 min.) | 25 ppm | 1ppm | Yes | Yes | No | Negative | No | N/A | Yes | No | No | Yes | Yes | Yes1 | Yes (30 min.) | 25 ppm | 1ppm | Yes | Negative | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes2 | Yes | No | Gas leak detection required unless "worse-case leak" cannot exceed 25% LFL in the ventilated enclosure.1 If gas leak detection is provided, excess flow control is not required.2
Disilane | Si2H6 | 3% | 1 | 4 | 2 |  | Pyrophoric (F4) Reactive (R2) | Oxygen, oxidizers, halogens, bromine, carbon tetrachloride, sulfur hexafluoride, chloroform, chlorine, fluorine, potassium hydroxide, alkali materials. | 19,200 ppm | N/A | Yes | Yes | Yes (10 sec.) | 500 ppm | 2.5ppm | Yes | Yes | Yes | <1.0% SiH4/Air Conc.1 | Yes | >1.4% SiH4/Air Conc (Alarm Only).2 | Yes | Yes | Yes (≤0.25 mm/0.01in)3 | Yes | Yes | Yes4 | Yes5 | 500 ppm | 2.5ppm | Yes | <1.0% SiH4/Air Conc.1,6 | Yes7 | >1.4% SiH4/Air Conc (Alarm Only).2 | Yes | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes | Yes | No | A worse-case leak shall not exceed a SiH4 to air ratio of greater than 1.0%.1 A loss of exhaust resulting in the possibility that the SiH4 to air concentration within the enclosure will exceed 1.4%2 RFO size limitation is for indoor storage/dispense. For exterior storage/dispense, RFO size shall not exceed 3.175 mm/0.125 in.3 Gas leak detection required when the delivery pressure within or to the enclosure exceeds 50 psi. It is also required when the gas line within the enclosure is <1/4” in dia.4 Gas leak detection above the critical level shall result in the shut off of the gas supply after it has validated there is a leak within the enclosure. If the delivery pressure exceeds 75 psi, automatic and immediate shutdown of the gas supply is required.5 The calculation for VMBs and tool gas boxes assumes the system complies with the TI standard for excess flow control valves, regulators and other protective measures in place that would have to fail before the SiH4 flow could reach the maximum allowed by the RFO. If the system does not have these protective measures (e.g., excess flow control valves, etc.) in place, then the site must calculate the amount of exhaust needed for the VMB or tool gas box based upon the source pressure and size of RFO installed on the system.6 Not required if the delivery pressure to a VMB or tool gas box does not exceed 50 psi. If the delivery pressure exceeds 50 psi, see note #2.7
Dimethylsilane | (CH3)2SiH2 | N/A | 1 | 4 | 1 |  | Flammable (F4) | Oxidizers, halogens, acids, alkalis. | 19,200 ppm | N/A | Yes | Yes | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | Yes1 | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Negative | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes2 | No | No | Gas leak detection required unless "worse-case leak" cannot exceed 25% LFL in the ventilated enclosure.1 If gas leak detection is provided, excess flow control is not required.2
Difluoromethane | CH2F2 | N/A | 0 | 4 | 0 |  | Flammable (F4) | Reactive metals, strong reducing and oxidizing agents. | >999K ppm | N/A | Yes | Yes | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | Yes1 | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Negative | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes2 | No | No | Gas leak detection required unless "worse-case leak" cannot exceed 25% LFL in the ventilated enclosure.1 If gas leak detection is provided, excess flow control is not required.2
>92% Fluorine | >92% F2 | N/A | 4 | 0 | 4 |  | Highly Toxic (H4) Unstable Reactive 3D (R4) Water Reactive (W, R4) | Water, all inorganic and organic substances. . | 185 ppm | 0.035-3 ppm | Yes | Yes | Yes (10 min.) | 12.5 ppm | 0.05ppm | Yes | Yes | Yes | 200 lfpm avg. (150 lfpm min.) | Yes | Yes (Alarm) | Yes | Yes | Yes1 | Yes | Yes | Yes | Yes (10 min.) | 12.5 ppm | 0.05ppm | Yes | 200 lfpm avg. (150 lfpm min.) | Yes | Yes (Alarm) | Yes | Yes | Yes | Yes | Yes | Yes (5 min.) | 0.1ppm | 0.05ppm | N | Yes | Yes | Yes | The RFO shall be sized no greater than 110% the maximum flow required for production.1
20% Fluorine in Nitrogen | 20% F2 in N2 | N/A | 3 | 0 | 0 |  | Toxic (H3) | Water, all inorganic and organic substances. . | 935 ppm | 0.035-3 ppm | Yes | No 1 | N/A | N/A | N/A | N/A | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | No 1 | N/A | N/A | N/A | N/A | Negative | No | N/A | No | No | Yes | Yes | No | N/A | N/A | N/A | N | Yes2 | Yes | No | Leak detection should be considered for equipment protection.1 If gas leak detection is provided, excess flow control is not required.2
1% Fluorine/Argon/Neon | 1% F2 in Ar/Ne | N/A | 2 | 0 | 1 |  | Non-Flammable Gas | Dilute concentration lessens the incompatibility hazards (See >92% F2). | 18519 ppm | 0.035-3 ppm | N/A | [14 empty] | N/A | [12 empty] | N/A |  |  |  |  | N/A
<1% Fluorine in Krypton/Neon | <1% F2 in Kr/Ne | N/A | 2 | 0 | 1 |  | Non-Flammable Gas | Dilute concentration lessens the incompatibility hazards (See >92% F2). | >18519 ppm | 0.035-3 ppm | N/A | [14 empty] | N/A | [12 empty] | N/A |  |  |  |  | N/A
~6% Germane in Hydrogen | ~6% GeH4 in H2 | 12..4% | 4 | 4 | 3 |  | Flammable (F4) Water Reactive (W, R3) | Oxidizing materials, bromine. | 10752 ppm | N/A | Yes | Yes | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | Yes3 | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Negative | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes4 | No | No | If monitoring for H2, this level results in a concentration of 140 ppm of GeH4.1 14 ppm H2 equals 200 ppb of GeH4 in concentration.2 Gas leak detection required unless "worse-case leak" cannot exceed 25% LFL in the ventilated enclosure.3 If gas leak detection is provided, excess flow control is not required.4
>75% Germanium Tetrahydride | >75% GeH4 | 12..4% | 4 | 4 | 3 |  | Highly Toxic (H4) Pyrophoric (F4) Water Reactive (W, R3) | Halogens, air. | 150 ppm | N/A | Yes | Yes | Yes (10 min.) | 3 ppm | 0.1 ppm | Yes | Yes | Yes | 200 lfpm avg. (150 lfpm min.) | Yes | Alarm Only | Yes | Yes | Yes (≤0.25 mm/0.01in)3 | Yes | Yes | Yes | Yes (10 min.) | 3 ppm | 0.1 ppm | Yes | 200 lfpm avg. (150 lfpm min.) | Yes | Alarm Only | Yes | Yes | Yes | Yes | Yes | Yes (10 sec.) | 0.2 ppm | 0.1 ppm | Y | Yes | No | Yes | RFO size limitation is for indoor storage/dispense. For exterior storage/dispense, RFO size shall not exceed 3.175 mm/0.125 in.1
Germanium Tetrafluoride VAC | GeF4 | N/A | 3 | 0 | 2 |  | Toxic (H3) Unstable Reactive (R2) | Halogens, air. | 1300 ppm | N/A | Yes1 | No | N/A | N/A | N/A | N/A | Yes1 | No | Negative | No | N/A | No | N/A1 | N/A1 | Yes | Yes | No | N/A | N/A | N/A | N/A | Negative | No | N/A | No | No | Yes | Yes | No | N/A | N/A | N/A | N/A | N/A2 | N/A2 | N/A2 | This is referencing the storage of VAC or Uptime cylinders.1 VAC and Uptime systems have proprietary designs that meet these requirements.2
99.95% Helium in Oxygen | 99.95% He in O2 |  | 0 | 0 | 0 |  | Non-Flammable Gas | None | N/A | N/A | N/A | [14 empty] | N/A | [12 empty] | N/A |  |  |  |  | N/A
Hexafluoroethane | C2F6 | N/A | 1 | 0 | 0 |  | Simple Asphyxiant | Alkali and alkaline earth metals | >280K ppm | Odorless | N/A | [14 empty] | N/A | [12 empty] | N/A |  |  |  |  | N/A
>99% Hydrogen Chloride | HCl | N/A | 3 | 0 | 1 |  | Non-Flammable Gas | Cyanides, metals, amines, bases, metal carbide, oxidizing materials, acids, halo carbons, combustible materials, halogens, metal salts | 3120 ppm | 1-5 ppm | Yes | No 1 | N/A | N/A | N/A | N/A | Yes | No | Negative | No | N/A | Yes | No | No | Yes | Yes | No 1 | N/A | N/A | N/A | N/A | Negative | No | N/A | No | No | Yes | Yes | No | N/A | N/A | N/A | N | Yes2 | Yes | No | Leak detection should be considered for equipment protection.1 If gas leak detection is provided, excess flow control is not required.2
Hydrogen | H2 | N/A | 1 | 4 | 0 |  | Flammable (F4) | Oxygen, oxidizing agents. | N/A | Odorless | Yes | Yes | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | Yes1 | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Negative | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes2 | No | No | Gas leak detection required unless "worse-case leak" cannot exceed 25% LFL in the ventilated enclosure.1 If gas leak detection is provided, excess flow control is not required.2
Hydrogen Bromide | HBr | N/A | 3 | 0 | 0 |  | Non-Flammable Gas | Water, fluorine, ferric oxide, ammonia, ozone. | 2858 ppm | 2-6 ppm | Yes | No 1 | N/A | N/A | N/A | N/A | Yes | No | Negative | No | N/A | Yes | No | No | Yes | Yes | No 1 | N/A | N/A | N/A | N/A | Negative | No | N/A | No | No | Yes | Yes | No | N/A | N/A | N/A | N | Yes2 | Yes | No | Leak detection should be considered for equipment protection.1 If gas leak detection is provided, excess flow control is not required.2
Hydrogen Fluoride | HF | N/A | 4 | 0 | 1 |  | Toxic (H3) | Carbonates, .sulfides, cyanides, alkalis, some oxides, common metals. | 1300 ppm | 0.5-3 ppm | Yes | No 1 | N/A | N/A | N/A | N/A | Yes | No | Negative | No | N/A | Yes | No | No | Yes | Yes | No 1 | N/A | N/A | N/A | N/A | Negative | No | N/A | No | No | Yes | Yes | No | N/A | N/A | N/A | N | Yes2 | Yes | No | Leak detection should be considered for equipment protection.1 If gas leak detection is provided, excess flow control is not required.2
≤5.7% Hydrogen in Helium/Argon/Nitrogen | ≤5.7% H2 in He/Ar/N2 | N/A | 0 | 0 | 0 |  | Non-Flammable Gas | None | N/A | N/A | N/A | [14 empty] | N/A | [12 empty] | N/A |  |  |  |  | N/A
≥5.7% Hydrogen in Nitrogen | ≥5.7% H2 in N2 | N/A | 1 | 4 | 0 |  | Flammable (F4) | Oxygen, oxidizing agents. | N/A | N/A | Yes | Yes | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | Yes1 | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Negative | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes2 | No | No | Gas leak detection required unless "worse-case leak" cannot exceed 25% LFL in the ventilated enclosure.1 If gas leak detection is provided, excess flow control is not required.2
Methane | CH4 | N/A | 1 | 4 | 0 |  | Flammable (F4) | Strong oxidizers. | N/A | Odorless | Yes | Yes | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | Yes1 | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Negative | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes2 | No | No | Gas leak detection required unless "worse-case leak" cannot exceed 25% LFL in the ventilated enclosure.1 If gas leak detection is provided, excess flow control is not required.2
≥7.7% Methane in Argon | 10% CH4 in Ar | N/A | 0 | 4 | 0 |  | Flammable (F4) | Strong oxidizers. | N/A | Odorless | Yes | Yes | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | Yes1 | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Negative | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes2 | No | No | Gas leak detection required unless "worse-case leak" cannot exceed 25% LFL in the ventilated enclosure.1 If gas leak detection is provided, excess flow control is not required.2
Methyl Fluoride | CH3F | N/A | 1 | 4 | 0 |  | Flammable (F4) Simple Asphyxiant | Oxidizers. | N/A | N/A | Yes | Yes | Yes (30 min.) | 500ppm | 250ppm | Yes | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | Yes1 | Yes (30 min.) | 500ppm | 250ppm | Yes | Negative | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes2 | No | No | Gas leak detection required unless "worse-case leak" cannot exceed 25% LFL in the ventilated enclosure.1 If gas leak detection is provided, excess flow control is not required.2
Methyl Silane | CH3SiH3 | N/A | 2 | 4 | 1 |  | Flammable (F4) | Oxidizers, halogens. | >5000 ppm | N/A | Yes | Yes | Yes (30 min.) | 5ppm | 2.5ppm | Yes | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | Yes1 | Yes (30 min.) | 5ppm | 2.5ppm | Yes | Negative | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes2 | No | No | Gas leak detection required unless "worse-case leak" cannot exceed 25% LFL in the ventilated enclosure.1 If gas leak detection is provided, excess flow control is not required.2
Nitric Oxide | NO | N/A | 3 | 0 | 0 |  | Toxic (H3) Oxidizer | Air, oxygen, flammable or combustible materials, powdered aluminum, boron, chlorine monoxide, chromium, fluorine, nitrogen trichloride, ozone, phosphorous, oxidizing agents, halogens, powdered iron, sodium monoxide, magnesium, manganese, uranium, tungsten carbide. | 870 ppm | 0.3-1 ppm | Yes | No | N/A | N/A | N/A | N/A | Yes | No | Negative | No | N/A | Yes | No | No | Yes | Yes | No | N/A | N/A | N/A | N/A | Negative | No | N/A | No | No | Yes | Yes | No | N/A | N/A | N/A | N | Yes1 | No | No | If gas leak detection is provided, excess flow control is not required.1
Nitrous Oxide | N2O |  | 1 | 0 | 0 |  | Oxidizer | Flammable materials, oils, grease, alkali metals, aluminum, boron, tin oxide, lithium hydride tungsten carbide, phosphine, ammonia, carbon monoxide, hydrogen sulfide, hydrogen, acetylene, catalytic surfaces. | N/A | N/A | N/A | [14 empty] | N/A | [12 empty] | N/A |  |  |  |  | N/A
Nitrogen Trifluoride | NF3 | N/A | 2 | 0 | 1 |  | Oxidizer | Reducing agents, hydrogen, ammonia, carbon monoxide, diborane, hydrogen, hydrogen sulfide, methane, tetrafluorohydrazine, charcoal and hydrogen-containing compounds, metals, oil, grease and other hydrocarbon materials. | 6700 ppm | N/A | Yes | No2 | Shutdown Not Required | N/A | N/A | No | No | No | Negative | No | N/A | Yes | No | No | Yes | Yes | No2 | Shutdown Not Required | N/A | N/A | No | Negative | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A | N | Yes1 | No | No | If gas leak detection is provided, excess flow control is not required.1 Leak detection should be considered for equipment protection.2
Octafluorocyclobutane | C4F8 | N/A | 0 | 0 | 0 |  | Simple Asphyxiant | Polystyrene, alkaline and alkaline earth metals, silver, brass, bonze, copper, alloys which contain more than 2% magnesium. | N/A | N/A | N/A | [14 empty] | N/A | [12 empty] | N/A |  |  |  |  | N/A
Octafluorocyclopentene | C5F8 | N/A | 3 | 0 | 1 |  | Toxic (H3) | Strong oxidizers, alkali and alkaline earth metals, powdered metals. | 1124 ppm | N/A | Yes | No | N/A | N/A | N/A | N/A | Yes | No | Negative | No | N/A | Yes | No | No | Yes | Yes | No | N/A | N/A | N/A | N/A | Negative | No | N/A | No | No | Yes | Yes | No | N/A | N/A | N/A | N | Yes1 | No | No | If gas leak detection is provided, excess flow control is not required.1
Ozone | O3 | N/A | 4 | 0 | 3 |  | Highly Toxic (H4) Unstable Reactive 3N (R3) | Combustibles, flammables, oxidizers. | 10 ppm | 0.0005-0.5 ppm | Yes1 | No | N/A | N/A | N/A | N/A | N/A | N/A | 200 lfpm avg. | No | N/A | N/A | N/A | N/A | Yes | Yes | Yes | Yes (10 min.) | 2.5 ppm | 100 ppb | Yes | 200 lfpm avg. | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | No | No | Yes2 | The ozone generator cabinet must be exhausted.1 Double-contained piping not required if the entire length of piping is welded, seamless stainless steel.2
Pentafluoroethane | CHF2CF3 |  | 2 | 1 | 0 |  | Simple Asphyxiant | Freshly abraded aluminum surfaces, reactive metals. | >160k ppm | N/A | N/A | [14 empty] | N/A | [12 empty] | N/A |  |  |  |  | N/A
>66% Perfluorobutadiene Hexafluorocyclobutadiene | >66% C4F6 | N/A | 3 | 4 | 0 |  | Toxic - Poor Warning Properties (H4) Flammable (F4) | Oxidizers, alkali or alkaline earth metals. | 1334 ppm | Odorless | Yes | Yes | Yes (10 min.) | 12.5 ppm | 0.25ppm | Yes | Yes | Yes | 200 lfpm avg. (150 lfpm min.) | Yes | Alarm Only | Yes | Yes | Yes1 | Yes | Yes | Yes | Yes (10 min.) | 12.5 ppm | 0.25ppm | Yes | 200 lfpm avg. (150 lfpm min.) | Yes | Alarm Only | Yes | Yes | Yes | Yes | Yes | Yes (5 min.) | 0.5ppm | 0.25ppm | N | Yes | Yes | Yes | The RFO shall be sized no greater than 110% the maximum flow required for production.1
>10% Phosphine "Hi-Pressure" | >10% PH3 | 2.2% | 4 | 4 | 2 |  | Highly Toxic (H4) Pyrophoric (F4) Unstable Reactive (R2) | Halogens, oxidizers, mercury(II) nitrate, boron trichloride, iodine, metal nitrates. | 20 ppm | 30 ppb | Yes | Yes | Yes (10 min.) | 25 ppm | .025ppm | Yes | Yes | Yes | 200 lfpm avg. (150 lfpm min.) | Yes | Alarm Only | Yes | Yes | Yes (≤0.25 mm/0.01in)1 | Yes | Yes | Yes | Yes (10 min.) | 25 ppm | .025ppm | Yes | 200 lfpm avg. (150 lfpm min.) | Yes | Alarm Only | Yes | Yes | Yes | Yes | Yes | Yes (5 min.) | 0.15ppm | .025ppm | N | Yes | Yes | Yes | RFO size limitation is for indoor storage/dispense. For exterior storage/dispense, RFO size shall not exceed 3.175 mm/0.125 in.1
>10% Phosphine SDS | >10% PH3 | 2.2% | 4 | 4 | 2 |  | Highly Toxic (H4) Flammable (F4) Unstable Reactive (R2) | Halogens, oxidizers, mercury(II) nitrate, boron trichloride, iodine, metal nitrates. | 20 ppm | 30 ppb | Yes1 | Yes1 | (Alarm Only)1 | 25 ppm | .025ppm | Yes | Yes1 | N/A1 | 200 lfpm avg. (150 lfpm min.) | No1 | N/A1 | Yes | N/A1 | N/A1 | Yes | Yes | Yes | Yes (10 min.) | 25 ppm | .025ppm | Yes | 200 lfpm avg. (150 lfpm min.) | Yes | Alarm Only | Yes2 | Yes | Yes | Yes | Yes | Yes (5 min.) | 0.15ppm | .025ppm | N/A | N/A3 | N/A3 | N/A3 | This is referencing the storage of SDS and Uptime cylinders.1 The tool monitoring the exhaust meets this requirement, if provided.2 SDS and Uptime systems have proprietary designs that meet these requirements.3
25 ppm Phosphine in Hydrogen | 25 ppm PH3 in H2 | 2.2% | 2 | 4 | 0 |  | Flammable (F4) | Halogens, oxidizers, mercury(II) nitrate, boron trichloride, iodine, metal nitrates. | ~800,000 ppm | 30 ppb | Yes | Yes | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | Yes3 | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Negative | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes4 | No | No | If monitoring for H2, this level results in a concentration of 250 ppb of PH3.1 6000 ppm H2 equals 150 ppb of PH3 in concentration.2 Gas leak detection required unless "worse-case leak" cannot exceed 25% LFL in the ventilated enclosure.3 If gas leak detection is provided, excess flow control is not required.4
0.8% Phosphine in Hydrogen | 0.8% PH3 in H2 | 2.2% | 4 | 4 | 2 |  | Flammable (F4) | Halogens, oxidizers, mercury(II) nitrate, boron trichloride, iodine, metal nitrates. | 2500 ppm | 30 ppb | Yes | Yes | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Yes | No | Negative | No | N/A | Yes | No | No | Yes | Yes | Yes3 | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Negative | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes4 | No | No | If monitoring for H2, this level results in a concentration of 80 ppm of PH3.1 37.5 ppm H2 equals 300 ppb of PH3 in concentration.2 Gas leak detection required unless "worse-case leak" cannot exceed 25% LFL in the ventilated enclosure.3 If gas leak detection is provided, excess flow control is not required.4
0.8% Phosphine in Helium | 0.8% PH3 in He | 2.2% | 4 | 0 | 2 |  | Unstable Reactive (R2) | Halogens, oxidizers, mercury(II) nitrate, boron trichloride, iodine, metal nitrates. | 2500 ppm | 30 ppb | N/A | [14 empty] | N/A | [12 empty] | N/A |  |  |  |  | N/A
0.8% Phosphine in Nitrogen | 0.8% PH3 in N2 | 2.2% | 4 | 0 | 2 |  | Unstable Reactive (R2) | Halogens, oxidizers, mercury(II) nitrate, boron trichloride, iodine, metal nitrates. | 2500 ppm | 30 ppb | N/A | [14 empty] | N/A | [12 empty] | N/A |  |  |  |  | N/A
5% Phosphine in Nitrogen | 5% PH3 in N2 | 2.2% | 4 | 4 | 2 |  | Toxic (H3) Flammable (F4) Unstable Reactive (R2) | Halogens, oxidizers, mercury(II) nitrate, boron trichloride, iodine, metal nitrates. | 1000 ppm | 30 ppb | Yes | Yes | Yes (30 min.) | 25 ppm | .025ppm | Yes | Yes | No | Negative | No | N/A | Yes | No | No | Yes | Yes | Yes | Yes (30 min.) | 25 ppm | .025ppm | Yes | Negative | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A | N | Yes1 | No | No | If gas leak detection is provided, excess flow control is not required.1
50% Phosphine in Silane | 50% PH3 in SiH4 | 2.2% | 4 | 4 | 3 |  | Highly Toxic (H4) Pyrophoric (F4) Unstable Reactive 3D (R3) | Halogens, oxidizers, mercury(II) nitrate, boron trichloride, heavy-metal halides, oxygen, bases. | 40 ppm | 30 ppb | Yes | Yes | Yes (10 sec.) | 25 ppm | .025ppm | Yes | Yes | Yes | <1.0% SiH4/Air Conc.2 | Yes | >1.4% SiH4/Air Conc. (Alarm)3 | Yes | Yes | Yes (≤0.25 mm/0.01in)4 | Yes | Yes | Yes5 | Yes (See Note)6 | 25 ppm | .025ppm | Yes | <1.0% SiH4/Air Conc.2,7 | Yes | >1.4% SiH4/Air Conc (Alarm).3 | Yes | Yes | Yes | Yes | Yes | Yes (5 min.) | 0.15ppm | .025ppm | Y | Yes | Yes | Yes | Warning and Critical limit established in gas cabinet and ventilated enclosure based upon PH3. Warning limit in fab area based upon 1/2 the TI OEL for PH3. 1 A worse-case leak shall not exceed a SiH4 to air ratio of greater than 1.0%.2 A loss of exhaust resulting in the possibility that the SiH4 to air concentration within the enclosure will exceed 1.4%3 RFO size limitation is for indoor storage/dispense. For exterior storage/dispense, RFO size shall not exceed 3.175 mm/0.125 in.4 Gas leak detection required when the delivery pressure within or to the enclosure exceeds 50 psi. It is also required when the gas line within the enclosure is <1/4” in dia.5 Gas leak detection above the critical level shall result in the shut off of the gas supply after it has validated there is a leak within the enclosure. If the delivery pressure exceeds 75 psi, automatic and immediate shutdown of the gas supply is required.6 The calculation for VMBs and tool gas boxes assumes the system complies with the TI standard for excess flow control valves, regulators and other protective measures in place that would have to fail before the SiH4 flow could reach the maximum allowed by the RFO. If the system does not have these protective measures (e.g., excess flow control valves, etc.) in place, then the site must calculate the amount of exhaust needed for the VMB or tool gas box based upon the source pressure and size of RFO installed on the system.7
Phosphorus Trifluoride | PF3 |  | 3 | 0 | 2 |  | Water Reactive (COR) | Most metallic materials and some plastics. | 320 ppm | N/A | Yes | No 1 | N/A | N/A | N/A | N/A | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | No 1 | N/A | N/A | N/A | N/A | Negative | No | N/A | No | No | Yes | Yes | No | N/A | N/A | N/A | N | Yes2 | Yes | No | Leak detection should be considered for equipment protection.1 If gas leak detection is provided, excess flow control is not required.2
Silicon Tetrachloride | SiCl4 | N/A | 3 | 0 | 2 |  | Non-Flammable Gas | Combustibles, metals. | 16,000 ppm | N/A | Yes | No | N/A | N/A | N/A | N/A | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | No | N/A | N/A | N/A | N/A | Negative | No | N/A | No | No | Yes | Yes | No | N/A | N/A | N/A | N | Yes1 | Yes | No | If gas leak detection is provided, excess flow control is not required.1
Silicon Tetrafluoride | SiF4 | N/A | 3 | 0 | 2 |  | Toxic (H3) | Alkali and alkaline earth metals, water, lithium nitride. | 450 ppm | N/A | Yes | No | N/A | N/A | N/A | N/A | Yes | No | Negative | No | N/A | Yes | No | No | Yes | Yes | No | N/A | N/A | N/A | N/A | Negative | No | N/A | No | No | Yes | Yes | No | N/A | N/A | N/A | N | Yes1 | Yes | No | If gas leak detection is provided, excess flow control is not required.1
"Silane" - Silcon Tetrahydride (SiH4) | SiH4 | 3% | 1 | 4 | 2 |  | Pyrophoric (F4) Reactive (R2) | Heavy-metal halides, free halogens, oxygen, oxidizers, bases. | 9600 ppm | N/A | Yes | Yes | Yes (10 sec.) | 2500 ppm | 2.5ppm | Yes | Yes | Yes | <1.0% SiH4/Air Conc.1 | Yes | >1.4% SiH4/Air Conc. (Alarm)2 | Yes | Yes | Yes (≤0.25 mm/0.01in)3 | Yes | Yes | Yes4 | Yes (See Note)5 | 2500 ppm | 2.5ppm | Yes | <1.0% SiH4/Air Conc.1,6 | Yes7 | >1.4% SiH4/Air Conc (Alarm).2 | Yes | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes | Yes | No | A worse-case leak shall not exceed a SiH4 to air ratio of greater than 1.0%.1 A loss of exhaust resulting in the possibility that the SiH4 to air concentration within the enclosure will exceed 1.4%2 RFO size limitation is for indoor storage/dispense. For exterior storage/dispense, RFO size shall not exceed 3.175 mm/0.125 in.3 Gas leak detection required when the delivery pressure within or to the enclosure exceeds 50 psi. It is also required when the gas line within the enclosure is <1/4” in dia.4 Gas leak detection above the critical level shall result in the shut off of the gas supply after it has validated there is a leak within the enclosure. If the delivery pressure exceeds 75 psi, automatic and immediate shutdown of the gas supply is required.5 The calculation for VMBs and tool gas boxes assumes the system complies with the TI standard for excess flow control valves, regulators and other protective measures in place that would have to fail before the SiH4 flow could reach the maximum allowed by the RFO. If the system does not have these protective measures (e.g., excess flow control valves, etc.) in place, then the site must calculate the amount of exhaust needed for the VMB or tool gas box based upon the source pressure and size of RFO installed on the system.6 Not required if the delivery pressure to a VMB or tool gas box does not exceed 50 psi. If the delivery pressure exceeds 50 psi, see note #2.7
20% Silane in Helium | 20% SiH4 in He | 3% | 1 | 4 | 2 |  | Pyrophoric (F4) Reactive (R2) | Heavy-metal halides, free halogens, oxygen, oxidizers, bases. | 19,200 ppm | Odorless | Yes | Yes | Yes (10 sec.) | 2500 ppm | 2.5ppm | Yes | Yes | Yes | <1.0% SiH4/Air Conc.1 | Yes | >1.4% SiH4/Air Conc. (Alarm)2 | Yes | Yes | Yes (≤0.25 mm/0.01in)3 | Yes | Yes | Yes4 | Yes (See Note)5 | 2500 ppm | 2.5ppm | Yes | <1.0% SiH4/Air Conc.1,6 | Yes7 | >1.4% SiH4/Air Conc (Alarm).2 | Yes | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes | Yes | No | A worse-case leak shall not exceed a SiH4 to air ratio of greater than 1.0%.1 A loss of exhaust resulting in the possibility that the SiH4 to air concentration within the enclosure will exceed 1.4%2 RFO size limitation is for indoor storage/dispense. For exterior storage/dispense, RFO size shall not exceed 3.175 mm/0.125 in.3 Gas leak detection required when the delivery pressure within or to the enclosure exceeds 50 psi. It is also required when the gas line within the enclosure is <1/4” in dia.4 Gas leak detection above the critical level shall result in the shut off of the gas supply after it has validated there is a leak within the enclosure. If the delivery pressure exceeds 75 psi, automatic and immediate shutdown of the gas supply is required.5 The calculation for VMBs and tool gas boxes assumes the system complies with the TI standard for excess flow control valves, regulators and other protective measures in place that would have to fail before the SiH4 flow could reach the maximum allowed by the RFO. If the system does not have these protective measures (e.g., excess flow control valves, etc.) in place, then the site must calculate the amount of exhaust needed for the VMB or tool gas box based upon the source pressure and size of RFO installed on the system.6 Not required if the delivery pressure to a VMB or tool gas box does not exceed 50 psi. If the delivery pressure exceeds 50 psi, see note #2.7
20% Silane in Nitrogen | 20% SiH4 in N2 | 3% | 1 | 4 | 2 |  | Pyrophoric (F4) Reactive (R2) | Heavy-metal halides, free halogens, oxygen, oxidizers, bases. | 19,200 ppm | Odorless | Yes | Yes | Yes (10 sec.) | 2500 ppm | 2.5ppm | Yes | Yes | Yes | <1.0% SiH4/Air Conc.1 | Yes | >1.4% SiH4/Air Conc. (Alarm)2 | Yes | Yes | Yes (≤0.25 mm/0.01in)3 | Yes | Yes | Yes4 | Yes (See Note)5 | 2500 ppm | 2.5ppm | Yes | <1.0% SiH4/Air Conc.1,6 | Yes7 | >1.4% SiH4/Air Conc (Alarm).2 | Yes | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes | Yes | No | A worse-case leak shall not exceed a SiH4 to air ratio of greater than 1.0%.1 A loss of exhaust resulting in the possibility that the SiH4 to air concentration within the enclosure will exceed 1.4%2 RFO size limitation is for indoor storage/dispense. For exterior storage/dispense, RFO size shall not exceed 3.175 mm/0.125 in.3 Gas leak detection required when the delivery pressure within or to the enclosure exceeds 50 psi. It is also required when the gas line within the enclosure is <1/4” in dia.4 Gas leak detection above the critical level shall result in the shut off of the gas supply after it has validated there is a leak within the enclosure. If the delivery pressure exceeds 75 psi, automatic and immediate shutdown of the gas supply is required.5 The calculation for VMBs and tool gas boxes assumes the system complies with the TI standard for excess flow control valves, regulators and other protective measures in place that would have to fail before the SiH4 flow could reach the maximum allowed by the RFO. If the system does not have these protective measures (e.g., excess flow control valves, etc.) in place, then the site must calculate the amount of exhaust needed for the VMB or tool gas box based upon the source pressure and size of RFO installed on the system.6 Not required if the delivery pressure to a VMB or tool gas box does not exceed 50 psi. If the delivery pressure exceeds 50 psi, see note #2.7
Sulfur Dioxide | SO2 | N/A | 3 | 0 | 0 |  | Corrosive (H3) Toxic poor warning properties (H3) | Strong bases, strong oxidizers, powdered metals, metal oxides, interhalogens, metal acetylides, sodium hydride, silver azide, cesium azide, fluorine, zinc, zinc compounds. | 2520 ppm | 0.67-4.75 ppm | Yes | No | No | N/A | N/A | N/A | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | No | N/A | N/A | N/A | N/A | Negative | No | N/A | No | No | Yes | Yes | No | No | N/A | N/A | N | Yes1 | No | No | If gas leak detection is provided, excess flow control is not required.1
Sulfur Hexafluoride | SF6 | N/A | 1 | 0 | 0 |  | Non-Flammable Gas | Disilane. | N/A | Odorless | N/A | [14 empty] | N/A | [17 empty] | N/A
Trifluoromethane | CHF3 | N/A | 2 | 0 | 1 |  | Non-Flammable Gas | Strong oxidizers, calcium, powdered aluminum, zinc, magnesium, beryllium, titanium, samarium, lithium, barium. | N/A | Odorless | N/A | [14 empty] | N/A | [17 empty] | N/A
"3MS" - Trimethylsilane ((CH3)3SiH) | (CH3)3SiH | N/A | 2 | 4 | 1 |  | Flammable (F4) | Oxidizers. | >5000 ppm | N/A | Yes | Yes | Yes (30 min.) | 2500 ppm | 2.5ppm | Yes | Yes | No | Negative | No | N/A | Yes | No | No | Yes | Yes | Yes | Yes (30 min.) | 2500 ppm | 2.5ppm | Yes | Negative | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes1 | No | No | If gas leak detection is provided, excess flow control is not required.1
Tungsten Hexafluoride (WF6) | WF6 | N/A | 4 | 0 | 2 |  | Water Reactive (COR) | Water | 217 ppm | N/A | Yes | No 1 | N/A | N/A | N/A | N/A | Yes | No | 200 lfpm avg. (150 lfpm min.) | Yes | Alarm Only | Yes | Yes | No | Yes | Yes | No 1 | N/A | N/A | N/A | N/A | 200 lfpm avg. (150 lfpm min.) | Yes | Alarm Only | Yes | Yes | Yes | Yes | No | N/A | N/A | N/A | N | Yes2 | Yes | No | Leak detection should be considered for equipment protection.1 If gas leak detection is provided, excess flow control is not required.2
Xenon (Xe) |  |  | 0 | 0 | 0 |  | Simple Asphyxiant | None. | N/A | N/A | N/A | [14 empty] | N/A | [12 empty] | N/A |  |  |  |  | N/A
Antimony Pentafluoride (solid) (SbF5) | SbF5 | N/A | 4 | 0 | 0 |  | Toxic | combustible materials, metals, reducing agents, water | N/A | N/A | Yes | Yes | Yes (10 min.) | 0.5 ppm | 0.25 ppm | Yes | Yes | Yes | 200 lfpm avg. (150 lfpm min.) | Yes | Alarm Only | Yes | Yes | Yes1 | Yes | Yes | Yes | Yes (10 min.) | 0.5 ppm | 0.25 ppm | Yes | 200 lfpm avg. (150 lfpm min.) | Yes | Alarm Only | Yes | No | Yes | Yes | Yes | Yes (5 min.) | 0.5 ppm | 0.25 ppm |  | Yes | No | Yes | The RFO shall be sized no greater than 110% the maximum flow required for production.1
Propene (Propylene) | C3H6 | NA | 1 | 4 | 1 |  | Flammable | Oxidizers, heat | >86 mg/l | 23 ppm | Yes | Yes | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | Yes1 | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Negative | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A |  | Yes2 | No | No | Gas leak detection required unless "worse-case leak" cannot exceed 25% LFL in the ventilated enclosure.1 If gas leak detection is provided, excess flow control is not required.2
Ethylene | C2H4 | NA | 2 | 4 | 2 |  | Flammable | Acids, halo carbons, halogens, metal salts, metals, oxidizing materials, peroxides | >64.5 mg/l | 270 ppm | Yes | Yes | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Yes | No | Negative | No | N/A | No | No | No | Yes | Yes | Yes1 | Yes (30 min.) | (25% of LEL) | (12.5% of LEL) | Yes | Negative | No | N/A | No | Yes | Yes | Yes | No | N/A | N/A | N/A |  | Yes2 | No | No | Gas leak detection required unless "worse-case leak" cannot exceed 25% LFL in the ventilated enclosure.1 If gas leak detection is provided, excess flow control is not required.2
Trisilane | Si3H8 | 2% | 1 | 4 | 2 | No contact with water | Pyrophoric (F4) Reactive (R2) | Sources of ignition, exposure to air. Trisilane has been reported as detonating in air. Decompositions Products: Thermal: Nitrogen oxides, silicon oxides, ammonia. Hydrolysis: ammonia and Silicon oxides. Trisilane is violently reactive with oxidizers and halogens. | N/A | N/A | Yes | Yes | Yes (10 sec.) | 2500 ppm | 2.5ppm | Yes | No | Yes | <1.0% SiH4/Air Conc.1 | Yes | >1.4% SiH4/Air Conc. (Alarm)2 | Yes | Yes | Yes (≤0.25 mm/0.01in)3 | Yes | Yes | Yes4 | Yes (See Note)5 | 2500 ppm | 2.5ppm | Yes | <1.0% SiH4/Air Conc.1,6 | Yes7 | >1.4% SiH4/Air Conc (Alarm).2 | Yes | Yes | Yes | Yes | No | N/A | N/A | N/A | Y | Yes | No | No | A worse-case leak shall not exceed a SiH4 to air ratio of greater than 1.0%.1 A loss of exhaust resulting in the possibility that the SiH4 to air concentration within the enclosure will exceed 1.4%2 RFO size limitation is for indoor storage/dispense. For exterior storage/dispense, RFO size shall not exceed 3.175 mm/0.125 in.3 Gas leak detection required when the delivery pressure within or to the enclosure exceeds 50 psi. It is also required when the gas line within the enclosure is <1/4” in dia.4 Gas leak detection above the critical level shall result in the shut off of the gas supply after it has validated there is a leak within the enclosure. If the delivery pressure exceeds 75 psi, automatic and immediate shutdown of the gas supply is required.5 The calculation for VMBs and tool gas boxes assumes the system complies with the TI standard for excess flow control valves, regulators and other protective measures in place that would have to fail before the SiH4 flow could reach the maximum allowed by the RFO. If the system does not have these protective measures (e.g., excess flow control valves, etc.) in place, then the site must calculate the amount of exhaust needed for the VMB or tool gas box based upon the source pressure and size of RFO installed on the system.6 Not required if the delivery pressure to a VMB or tool gas box does not exceed 50 psi. If the delivery pressure exceeds 50 psi, see note #2.7
Delays are allowed under the following conditions:
1) Emergency/Haz-Mat Response is dispatched immediately the affected area.
2) Portable equipment can verify there is no gas outside a cabinet or exhausted enclosure.
3) The gas cabinet or exhausted enclosure must be labeled indicating there is a leak and it is not to be opened until the situation is corrected or the gas is shut off.
4) Exhaust is functional
Note: Detector impairment allows for a 30 min. delay, as long as emergency/hazmat response is dispatched immediately (Delay is not allowed for pyrophoric concentrations).
Note on L5: Mike Alton: http://research.dfci.harvard.edu/ehs/PPE/Respirators/comparison_of_odor_thresholds_an.htm
Note on AU5: Not currently approved for fab use
Note on L6: Mike Alton: http://research.dfci.harvard.edu/ehs/PPE/Respirators/comparison_of_odor_thresholds_an.htm
Note on L8: Mike Alton: http://research.dfci.harvard.edu/ehs/PPE/Respirators/comparison_of_odor_thresholds_an.htm
Note on R8: Desai, Deven: Proposed detection value
Note on AU8: Desai, Deven: Proposed new detection values
Note on I9: Mike Alton: As defined by IFC2006, 50 ppm AsH3 in H2 is not toxic.
Note on L9: Mike Alton: http://research.dfci.harvard.edu/ehs/PPE/Respirators/comparison_of_odor_thresholds_an.htm
Note on I10: Mike Alton: As defined by IFC2006, 60 ppm AsH3 in H2 is not toxic.
Note on L10: Mike Alton: http://research.dfci.harvard.edu/ehs/PPE/Respirators/comparison_of_odor_thresholds_an.htm
Note on I11: Mike Alton: As defined by IFC2006, 600 ppm AsH3 in H2 is not toxic.
Note on L11: Mike Alton: http://research.dfci.harvard.edu/ehs/PPE/Respirators/comparison_of_odor_thresholds_an.htm
Note on I12: Mike Alton: As defined by IFC2006, 50 ppm AsH3 in N2 is not toxic
Note on L12: Mike Alton: http://research.dfci.harvard.edu/ehs/PPE/Respirators/comparison_of_odor_thresholds_an.htm
Note on L13: Mike Alton: http://research.dfci.harvard.edu/ehs/PPE/Respirators/comparison_of_odor_thresholds_an.htm
Note on L14: Mike Alton: Based upon HCL. Due to its tendency to fume in moist air, liberating HCl. Patty's Industrial Hygiene and Toxicology, 3rd Revised Edition, Volume IIB
Note on I15: 9/2020 Change from Toxic gas to toxic gas with poor warning properties based on update of TLV ceiling in 2018
Note on L15: Mike Alton: Patty's Industrial Hygiene and Toxicology, 3rd Revised Edition, Volume IIB
Note on AT15: Delay is not allowed due to 0.7 ppm ceiling
Note on I16: 9/2020 Change from Toxic gas to toxic gas with poor warning properties based on update of TLV ceiling in 2018
Note on L16: Mike Alton: Patty's Industrial Hygiene and Toxicology, 3rd Revised Edition, Volume IIB
Note on AT16: Delay is not allowed due to 0.7 ppm ceiling
Note on L17: Mike Alton: http://csi.micromedex.com/DATA/CH/CHCDO.HTM?Top=Yes
Note on L18: Mike Alton: Patty's Industrial Hygiene and Toxicology, 3rd Revised Edition, Volume IIB
Note on L20: Mike Alton: Patty's Industrial Hygiene and Toxicology, 3rd Revised Edition, Volume IIB
Note on L21: Mike Alton: Patty's Industrial Hygiene and Toxicology, 3rd Revised Edition, Volume IIB
Note on I22: Mike Alton: As defined by IFC2006, ~40 ppm B2H6 in H2 is not toxic.
Note on L22: Mike Alton: Patty's Industrial Hygiene and Toxicology, 3rd Revised Edition, Volume IIB
Note on L23: Mike Alton: Patty's Industrial Hygiene and Toxicology, 3rd Revised Edition, Volume IIB
Note on A24: Mike Alton: Based upon exposure limits for Hydrogen Chloride, which is a decomposition product.
Note on L24: Mike Alton: http://csi.micromedex.com/DATA/CH/CHHDC.HTM
Note on C25: Mike Alton: Based upon pyrophoric concentration of silane.
Note on L28: Mike Alton: http://research.dfci.harvard.edu/ehs/PPE/Respirators/comparison_of_odor_thresholds_an.htm
Note on L29: Mike Alton: http://research.dfci.harvard.edu/ehs/PPE/Respirators/comparison_of_odor_thresholds_an.htm
Note on L30: Mike Alton: http://research.dfci.harvard.edu/ehs/PPE/Respirators/comparison_of_odor_thresholds_an.htm
Note on L31: Mike Alton: http://research.dfci.harvard.edu/ehs/PPE/Respirators/comparison_of_odor_thresholds_an.htm
Note on E32: Mike Alton: The health & reactivity ratings are for Germane (100%). Per IFC2006, ~1.4% Germane is not toxic.
Note on L36: Mike Alton: http://csi.micromedex.com/DATA/NJ/NJ989.HTM?Top=Yes
Note on I37: Mike Alton: Per IFC2006, HCl is not considered a toxic gas.
Note on L37: Mike Alton: http://csi.micromedex.com/DATA/CH/CHHDC.HTM
Note on L38: Mike Alton: http://csi.micromedex.com/DATA/TM/TM577.HTM?Top=Yes
Note on I39: Mike Alton: As defined by IFC2006 HBr is not a toxic gas.
Note on L39: Mike Alton: Patty's Industrial Hygiene and Toxicology, 3rd Revised Edition, Volume IIB
Note on L40: Mike Alton: http://csi.micromedex.com/DATA/DT/DT118.HTM?Top=Yes
Note on L43: Mike Alton: http://csi.micromedex.com/DATA/TM/TM577.HTM?Top=Yes
Note on L44: Mike Alton: http://csi.micromedex.com/DATA/TM/TM577.HTM?Top=Yes
Note on K47: Mike Alton: Calculated from 1068 mg/m3
Note on L47: Mike Alton: http://csi.micromedex.com/DATA/NJ/NJ1357.HTM?Top=Yes
Note on G49: Mike Alton: Note: There is no written documentation to support that NF3 meets the definition of a Class 3 reactive (i.e., "Materials that in themselves are capable of detonation or of explosive decomposition or explosive reaction but which require a strong initiating source or which must be heated under confinement before initiation. This class includes materials that are sensitive to thermal or mechanical shock at elevated temperatures and pressures") TI feels the Air Liquide MSDS effective 1/1/05, which states NFPA Reactivity 3, is incorrect/a typo. NF3 is a very strong oxidizer that "...in themselves are normally stable but which can become unstable at elevated temperatures and pressure" and this should be considered a Class 1 reactive.
Note on L52: Mike Alton: http://research.dfci.harvard.edu/ehs/PPE/Respirators/comparison_of_odor_thresholds_an.htm
Note on AS52: Mike Alton: Due to the reactive nature of O3 in air, ambient monitoring for O3 at the work station does not seem feasible.
Note on E53: Mike Alton: http://www.aireco.com/MSDS/r125.pdf
Note on L54: Mike Alton: http://csi.micromedex.com/DATA/MS/MS373566.HTM#SECT9
Note on R54: Desai, Deven: Proposed detection value
Note on AH54: Desai, Deven: Proposed detection value
Note on L55: Mike Alton: http://csi.micromedex.com/DATA/TM/TM119.HTM?Top=Yes
Note on R55: Desai, Deven: Proposed detection value
Note on AH55: Desai, Deven: Proposed detection value
Note on AU55: Desai, Deven: Proposed detection value
Note on L56: Mike Alton: http://csi.micromedex.com/DATA/TM/TM119.HTM?Top=Yes
Note on R56: Desai, Deven: Proposed detection value
Note on AH56: Desai, Deven: Proposed detection value
Note on AU56: Desai, Deven: Proposed detection value
Note on L57: Mike Alton: http://csi.micromedex.com/DATA/TM/TM119.HTM?Top=Yes
Note on I58: Mike Alton: As defined by IFC2006, 0.8% PH3 in H2 is not toxic.
Note on L58: Mike Alton: http://csi.micromedex.com/DATA/TM/TM119.HTM?Top=Yes
Note on I59: Mike Alton: As defined by IFC2006, 0.8% PH3 in N2 is not toxic
Note on I60: Mike Alton: As defined by IFC2006, 0.8% PH3 in N2 is not toxic
Note on R61: Desai, Deven: Proposed detection value
Note on AH61: Desai, Deven: Proposed detection value
Note on L62: Mike Alton: http://csi.micromedex.com/DATA/TM/TM119.HTM?Top=Yes
Note on R62: Desai, Deven: Proposed detection value
Note on AH62: Desai, Deven: Proposed detection value
Note on AU62: Desai, Deven: Proposed detection value
Note on C66: Mike Alton: Based upon pyrophoric concentration of silane.
Note on R66: Desai, Deven: Proposed detection value
Note on AH66: Desai, Deven: Proposed detection value
Note on I69: 9/2020 Change from Toxic gas to toxic gas with poor warning properties based on update of TLV ceiling in 2018
Note on L70: Mike Alton: http://www.sayedsaad.com/substation/sf6_gas_properties.htm
Note on L71: Mike Alton: http://csi.micromedex.com/DATA/HS/HS5207D.htm
Note on C78: Mike Alton: Based upon pyrophoric concentration of silane.
Note on R78: Desai, Deven: Proposed detection value
Note on AH78: Desai, Deven: Proposed detection value

## Notes
TI ESH Standard / US Code Reference
Note 1: | A TI OEL is a health-based workplace standard exposure level established by a recognized government or research entity, at (or below) which workers are safe from adverse effects (e.g., OSHA Permissible Exposure Limit (PEL), American Congress of Government Industrial hygienists (ACGIH) TLV®, REL, WEEL, MAK, UK OEL). The TI established OEL is typically the most stringent of these levels unless there are other mitigating factors such as lack of available technology. Where a reliable OEL is not listed by any of these agencies for a specific chemical, an applicable Occupational Exposure Limit (OEL) will be determined from other available information. | See TI ESH Standard 03.01D Exposure Limits
Note 2: | A Short Term Exposure Limit (STEL) is defined by ACGIH as the concentration to which workers can be exposed continuously for a short period of time without suffering from: 1)irritation; 2) chronic or irreversible tissue damage or 3) narcosis of sufficient degree to increase the likelihood of accidental injury, impair self-rescue or materially reduce work efficiency. An STEL is not a separate independent exposure limit, but supplements time-weighted average limits where there are recognized acute effects from a substance whose toxic effects generally chronic (long-term) in nature. Workers can be exposed to a maximum of four STEL periods per 8 hour shift, with at least 60 minutes between exposure periods. | See TI ESH Standard 03.01D Exposure Limits
Note 3: | The Ceiling is an exposure limit of which at no time shall exceed the exposure limit given for that substance. If instantaneous monitoring is not feasible, then the ceiling shall be assessed as a 15-minute time weighted average exposure which shall not be exceeded at any time during the working day. | See TI ESH Standard 03.01D Exposure Limits
Note 4: | IDLH is a concentration of airborne contaminants, which poses a threat of death, immediate or delayed permanent adverse health effects or effects that could prevent an individual’s escape from such an environment. | See TI ESH Standard 03.01D Exposure Limits
Note 4a: | Breathing zone: The area near a persons that in their normal work posture most likely reflects the levels the worker might inhale | See TI ESH Standard 03.01D Exposure Limits
Note 5: | Median lethal concentration. The concentration of a material in air that on the basis of laboratory tests (respiratory route) is expected to kill 50% of a test population when administered as a singe exposure in a specific time period, usually 1 hr. Gases with an LC50 of 0 ppm to 200 ppm are considered highly toxic; gases with an LC50 of 201 ppm to 2000 ppm are considered toxic. For binary mixtures where the hazardous component is diluted with a nontoxic gas, the LC50 of the mixture is estimated by use of the following formula: LC50m = 1/[Ci/LC50i] For multi-component mixtures where more than one component has a listed LC50, the LC50 of the mixture is estimated by use of the following formula: C50m = 1/(Ci1/LC50i1)+(Cin/LC50in) | See TI ESH Standard 03.01D Exposure Limits
Note 6: | The odor detection threshold is lowest concentration of a certain odor compound that is perceivable by the human sense of smell. | See TI ESH Standard 03.01D Exposure Limits
Note 7: | Indicates whether, due to the hazardous nature of the gas/chemical contained within the cylinder/container or the delivery system, a gas/chemical cabinet or ventilated enclosure is required to ensure the safe storage of the cylinder/container or to ensure safe distribution of the cylinder/container and piping's contents. All gas/chemical cabinets and ventilated enclosures must have exhaust provided. NOTE(S): 1) Pertains to indoor storage and indoor distribution systems only. 2) Gas cylinder cabinets shall not be required for purge cylinder gases when installed within a gas cylinder room that has area gas leak detection. | International Fire Code Chapter 27
Note 8: | Indicates whether a gas/chemical leak detection sampling point is required within a gas/chemical cabinet, a ventilated enclosure or in the fab air space (ambient air - near the manufacturing equipment). NOTE: The gas/chemical leak detection point must be located within the exhaust line of the gas/chemical cabinet or ventilated enclosure and not within the gas/chemical cabinet or ventilated enclosure itself. Outside of the US, area (ambient) detection (points) shall be provided for pressurized HTG&TGWPWP (e.g., gas rooms, fab areas) unless the following requirements are met; 1. Gas source supply lines are doubled contained; 2. Exhausted enclosures are monitored for loss of exhaust pressure or flow; and 3. Gas leak detection is provided in the exhausted enclosure. | International Fire Code 2703.13.2.2
Note 9: | Upon a "critical level" leak detection, this section indicates if the gas/chemical delivery system can continue to function and, if so, for how long (i.e., continue supplying gas) before it must automatically and immediately shut off the gas/chemical supply at the next upstream pneumatic valve on the applicable delivery system. NOTE: If the gas/chemical concentration within the gas/chemical cabinet or exhausted enclosure exceeds 2X the critical level, it is recommended the gas/chemical supply be manually forced to shut down even if the allowed delay time has not been exceeded. | International Fire Code 2703.13
Note 10: | Indicates the gas/chemical to air concentration that cannot be exceeded without automatically and immediately shutting off the gas supply or initiating the automatic shut off of the gas supply within the time delay allowed and shall generate an alarm at a continuously monitored location and initiate a response. | International Fire Code 2703.13
Note 11: | Indicated the gas/chemical to air concentration that, when exceeded, should generate a warning alarm at a continuously monitored location and initiate a response. NOTE: This is a recommended level. If the site's gas/chemical leak detection equipment cannot reliably monitor a gas to air concentration at the level recommended, the site shall ensure the warning level is set to the gas/chemical leak detection equipment's lower detectable level. | International Fire Code 2703.13.2
Note 12: | Upon a gas/chemical leak detection at or above the warning level, there shall be an audible and visible alarm generated at the point of the gas leak alarm. The audible alarm shall be distinct from all other alarms. | International Fire Code 2703.13.2.1
Note 13: | The system is activated by heat from a fire and discharges water over the fire area.
Note 14: | Indicates the need for an "automatic cabinet", one which can automatically switch between on-line cylinders and can perform a gas line purge function via a computer (i.e., a control panel). NOTE: Required for distribution systems using a highly toxic gas, a toxic gas with poor warning properties or a pyrophoric gas. | International Fire Code 5003.8.6
Note 15: | Describes the amount of exhaust that must be pulled through the gas/chemical cabinet or the ventilated enclosure. For a highly toxic gas or a toxic gas with poor warning properties, the amount of exhaust required is determined by taking a velocity reading at the face of the gas cylinder cabinet or ventilated enclosure access port or window. For silane gases, the amount of exhaust required is determined by the leak rate from a worse-case leak, ensuring the silane-to-air concentration cannot exceed 1.0%. For all other gases, there shall be enough exhaust provided to ensure the interior space of the gas cylinder cabinet or ventilated enclosure remains at a negative pressure in relation to the surrounding area. | International Fire Code 2703.14
Note 16: | Requires that the exhaust flow within the gas/chemical cabinet or ventilated enclosure be monitored at a continuously monitored location and shall initiate system responses and alert appropriate personnel (e.g., facilities, security) upon loss of exhaust. | International Fire Code 2703.14.1
Note 16a | Liquid Storage warehouse storing containers greater than 5 gallons (19L) in capacity shall be ventilated at a rate of not less than 0.25 cfm per square foot (0.075 m3/s*m2) of floor area over the storage area | International Fire Code 5004.3
Note 17: | For highly toxic gases and toxic gases with poor warning properties, a loss of 25% of the required exhaust shall result in a warning alarm at the continuously monitored location and a site response. For silane gases, a loss of exhaust resulting in a potential silane-to-air concentration of 1.4% or greater shall result in a warning alarm at the continuously monitored location and a site response. | International Fire Code 2703.13.2
Note 18: | Requires that there be some visual mean present to indicate the exhaust provided to a gas cylinder cabinet or ventilated enclosure is present. Examples of visual indicators include magnehelics, pressure guages and streamers.
Note 19: | Device installed on a compressed gas cylinder or on each VMB gas distribution line that opens the gas cylinder valve port by applying pneumatic pressure (e.g., nitrogen, air - as appropriate for safety), and which returns to its closed position if the pneumatic pressure is removed or discharges through venting or melting of the pneumatic supply line. | For Silane, see Compress Gas Association Standard G13.
Note 20: | A device located in a gas cylinder or plumbing assembly that restricts the flow that can be discharged from the cylinder or piping during a leak. RFO sizes control the available flow (e.g., a 0.10 orifice allows a flow of 30 L/min (1.06 ft3/min)).
Note 21: | See below for explanation.
Note 22: | Indicates the gas to air concentration that cannot be exceeded in the fab air space without automatically and immediately shutting off the gas supply or initiating the automatic shut off of the gas supply within the time delay allowed. | International Fire Code 2703.13.2
Note 23: | Indicates that an excess flow control device is required on the delivery system, unless the "Special Notes" section indicates it can be eliminated because there is gas leak detection provided in the gas cylinder cabinet and in the ventilated enclosure(s). The excess flow device can be installed on the gas cylinder cabinet side of the delivery system. | ANSI/CGA G-13
Note 24: | Indicates that the need for a continuous N2 purge feeding the vent line of the gas cylinder cabinet and the VMB, if applicable.
Note 25: | Indicates the need for double-contained piping to be used throughout the entire gas distribution system. NOTE(S): 1. The annular space between the supply line tubing and the secondary containment tubing shall be under vacuum or pressurized with an inert gas; 2. The annular space shall be monitored for loss of vacuum or a change in pressure to indicate a leak; 3. A leak shall activate an alarm circuit which shall close the nearest upstream valve or gas cylinder supplying the tubing and send an alarm to a continuously monitored control station; and 4. The double-contained piping system shall be designed to ensure the annular space can be safely evacuated or vented in the event it becomes contaminated with a HTG or TGWPWP. | International Fire Code 5005.2.2.4
Note 26: | Pertaining to new or modified systems; gas cylinder cabinets and ventilated enclosures containing hazardous gases shall be provided with emergency shut off capability (e.g. EMO). If you EMO the cabinet (gas or VMB) it will only isolate all valves within the cabinet. A leak detection within the cabinet shall isolate the upstream valve.
Note 27: | Explosion control requirements are based on 2018 International Fire Code Table 911.1 "Explosion Control Requirements"
Note on C12: There maybe additional aggrements between the City of Dallas Fire and Rescue and TI North Campus Expressway

## Revision History
Date | Revision Made
2020-09-10 | Add revision history to appendix A
2020-09-10 | Change NFPA Classification BF3 from Corrosive Toxic to Corrosive Toxic with poor warning properties. Add breathing zone detection, evacuation level for the fab
2020-09-10 | Change NFPA Classification SO2 from non-flammable gas to toxic gas with poor warning properties. Add breathing zone detection, evacuation level for the fab
2020-11-12 | Add reference column on the Notes Page to allow US employees an additional reference for determining the requirements for proper installation.
2021-03-25 | Removed all TI OEL information. Add reference to the notes to see 03.01D for information on TI OEL's.
2021-03-25 | Add Antimony Pentraflouride
2021-03-29 | Added Liquid to Gas Chemical Information
2021-07-13 | Addition of Propene
2021-07-29 | Addition of Ethylene
2021-10-19 | Updated flammable limits, added back LC50 and odor threshold to matrix, Implement ELC approval and fan-out
2023-06-26 | Updated 1% Arsine in SDS bottle TI OEL values
2023-12-21 | Updated - 1. Detection values published within matrix 2. Aligment with IFC on detection values for highly toxic and toxic gases within breathing zone and exhausted enclosures 3. Values for 1% Arsine (Hi-pressure) 4. Ozone detection values 5. NF3 detection for asset protection purposes, not required by code 6. Impairment note at bottom of "Gases" tab, updated time delay to 30 mins for impairment